## String Sizing
String Sizing: 5 MWp PV plant (IEC 62548 checks)
Legend: fill the YELLOW cells in column C (blue = input). Column D is a worked example with generic values, not a real product. Formulas are in black. Record sources in ASSUMPTIONS.md.
Parameter | Unit | My design | Example (generic) | Source / note
Module model |  |  | Generic 550 Wp mono PERC (example) | Datasheet
Pmax (STC) | W |  | 550 | Datasheet
Voc (STC) | V |  | 49.8 | Datasheet
Vmp (STC) | V |  | 41.9 | Datasheet
Isc (STC) | A |  | 14 | Datasheet
β Voc | %/°C |  | -0.27 | Datasheet (negative)
β Vmp (or γ Pmax if not given) | %/°C |  | -0.35 | Datasheet; γ Pmax is a common approximation
α Isc | %/°C |  | 0.048 | Datasheet (positive)
NOCT / NMOT | °C |  | 45 | Datasheet
INVERTER
Inverter model |  |  | Generic 1500 V, 250 kW string inverter (example) | Datasheet
Rated AC power | kW |  | 250 | Datasheet
Max DC input voltage | V |  | 1500 | Datasheet: hard limit
MPPT min voltage | V |  | 500 | Datasheet
MPPT max voltage | V |  | 1500 | Datasheet
Number of MPPTs |  |  | 12 | Datasheet
Max short-circuit current per MPPT | A |  | 50 | Datasheet
SITE
Site |  |  | Example site, western West Bengal | Google Earth
Record minimum ambient temperature | °C |  | 3 | IMD / NASA POWER
Design maximum ambient temperature | °C |  | 45 | IMD / NASA POWER
DESIGN
Target DC capacity | kWp | 5000 | 5000 | Project scope
Target DC/AC ratio |  | 1.25 | 1.25 | Design choice
Bifacial rear gain on Isc | fraction | 0 | 0 | 0 for monofacial
Chosen modules per string (blank = max allowed) |  |  |  | Optional override
RESULTS
Min cell temperature | °C | 0 | 3
Max cell temperature (NOCT, 1000 W/m²) | °C | -25 | 76.25
Voc at min temperature | V | 0 | 52.7581
Vmp at max temperature | V | 0 | 34.3842
Vmp at min temperature | V | 0 | 45.1263
Isc at max temperature × bifacial gain | A | 0 | 14.3444
1.25 × Isc (cable/fuse basis) | A | 0 | 17.9305
Max modules/string (DC voltage limit) |  |  | 28
Min modules/string (MPPT min, hot) |  |  | 15
Max modules/string before MPPT max (cold) |  |  | 33
Chosen modules/string |  |  | 28
String Voc at min temperature | V |  | 1477.2274
String Vmp at max temperature | V |  | 962.7572
String Vmp at min temperature | V |  | 1263.5364
Max strings per MPPT |  |  | 3
Max strings per inverter |  |  | 36
String power | kWp |  | 15.4
Number of strings |  |  | 325
Number of modules |  |  | 9100
Actual DC capacity | kWp |  | 5005
Number of inverters |  |  | 16
Total AC capacity | kW |  | 4000
Actual DC/AC ratio |  |  | 1.2512
Strings per inverter |  |  | 21
CHECKS
String Voc(min T) ≤ max DC voltage |  |  | PASS
String Vmp(max T) ≥ MPPT min |  |  | PASS
String Vmp(min T) ≤ MPPT max |  |  | PASS
Strings/inverter ≤ MPPT current limit |  |  | PASS
Min ≤ chosen ≤ max modules/string |  |  | PASS
Note on C29: Leave blank to use the maximum string length allowed by the DC voltage limit.